## Sheet1
|  | Length | Byte Address | Hex Address |  | Range
0000H | Current combined total active energy | 4 | 0 | 0 | FFFFFFFF | 0 | to | 4294967295
0002H | Current combined spike active energy | 4 | 2 | 2 | FFFFFFFF | 0 | to | 4294967295
0004H | Current combined peak active energy | 4 | 4 | 4 | FFFFFFFF | 0 | to | 4294967295
0006H | Current combined flat active energy | 4 | 6 | 6 | FFFFFFFF | 0 | to | 4294967295
0008H | Current combinedvalue active energy | 4 | 8 | 8 | FFFFFFFF | 0 | to | 4294967295
000AH | Code | 2 | 10 | A | FFFF | 0 | to | 65535
000BH | Voltage | 2 | 11 | B | FFFF | 0 | to | 65535
000CH | Current | 2 | 12 | C | FFFF | 0 | to | 65535
000DH | Active Power | 2 | 13 | D | FFFF | 0 | to | 65535
000EH | Reactive Power | 2 | 14 | E | FFFF | 0 | to | 65535
000FH | Apparent Power | 2 | 15 | F | FFFF | 0 | to | 65535
0010H | Power Factor | 2 | 16 | 10 | FFFF | 0 | to | 65535
0011H | Frequency | 2 | 17 | 11 | FFFF | 0 | to | 65535
0012H | Year, Month | 2 | 18 | 12 | FFFF | HighByte = 0 to 99 = Year |  |  | LowByte= 1 to 12 Month
0013H | Day, Hour | 2 | 19 | 13 | FFFF | HighByte = 1 to 7 = Day |  |  | LowByte= 0 to 23 Hour
0014H | Minute, Second | 2 | 20 | 14 | FFFF | HighBye 0 to 59 Minute |  |  | LowByte 0 to 59 Seconds
0015H | Address | 1 | 21 | 15 |  | 0 | to | 254 | High byte
0015H | Communication Baud Rate | 1 | 21 | 15 |  | 00 | to | 04 | Low byte
0016H | Light time | 2 | 22 | 16 |  | 0 | to | 254
Which models of ADL support time? Does the clock work?
What fields are actually updated per model of ADL?
What is the format of the floats? It is not IEEE
Passive pulse output, conform to DIN43864 standard ? 5v0 10k Pullup?
What is PRG H01? 0701 ? Mean ?
L 86 0001 ?
What does CLRe clear?